## Sis69
Parameter | Value
Lifetime of branches. | 25
Upper bounds for the absolute value of {$\Delta_{ij,t}^V$} | 20
Cost coefficients for load shedding | 2
Cost coefficients expected energy non supplied | 0.0112
Cost coefficient for the energy supplied substation | 0.00013
Interest rate. | 0.1
Years into each stage | 10
Lower voltage limit | 0.95
Upper voltage limit | 1.05
Nominal voltage | 12.66
Demand factor of load level | 0.83
Number of discretizations | 15
*** costs are expression in K$
*** costs are expression in K$
From | To | Type of branch | Switching | Durations of the switching-only interruptions (h) | Durations of the repair-and-switching interruption (h) | Failure rate of branch | Resistence (Ω) | Reactance(Ω) | Maximum current flow magnitude (A) | Cost coefficients for the installation | Node | Active power demand (kW) | Reactive power demand (kW)
0 | 1 | Fixed | 1 | 0.5 | 5 | 0.5 | 0.001 | 0.001 | 150 | 0 | 0 | 0 | 0
1 | 2 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.001 | 0.001 | 150 | 0 | 1 | 0 | 0
2 | 3 | Fixed | 0 | 0.5 | 5 | 0.5 | 0 | 0 | 150 | 0 | 2 | 0 | 0
3 | 4 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.002 | 0.004 | 100 | 0 | 3 | 0 | 0
4 | 5 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.025 | 0.029 | 100 | 0 | 4 | 0 | 0
5 | 6 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.366 | 0.186 | 100 | 0 | 5 | 0 | 0
6 | 7 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.381 | 0.194 | 100 | 0 | 6 | 0.878 | 0.72
7 | 8 | Fixed | 1 | 0.5 | 5 | 0.5 | 0.092 | 0.047 | 100 | 0 | 7 | 13.455 | 9.982
8 | 9 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.049 | 0.025 | 100 | 0 | 8 | 24.887 | 17.81
9 | 10 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.819 | 0.271 | 100 | 0 | 9 | 10 | 7.208
10 | 11 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.187 | 0.062 | 100 | 0 | 10 | 9.333 | 6.666
11 | 12 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.711 | 0.235 | 100 | 0 | 11 | 48.5 | 34.609
12 | 13 | Fixed | 0 | 0.5 | 5 | 0.5 | 1.03 | 0.34 | 100 | 0 | 12 | 48.5 | 34.609
13 | 14 | Fixed | 0 | 0.5 | 5 | 0.5 | 1.044 | 0.345 | 100 | 0 | 13 | 2.71 | 1.821
14 | 15 | Fixed | 0 | 0.5 | 5 | 0.5 | 1.058 | 0.35 | 100 | 0 | 14 | 2.71 | 1.821
15 | 16 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.197 | 0.065 | 100 | 0 | 15 | 0 | 0
16 | 17 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.374 | 0.124 | 100 | 0 | 16 | 15.176 | 10.198
17 | 18 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.005 | 0.002 | 100 | 0 | 17 | 16.5 | 11.775
18 | 19 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.328 | 0.108 | 100 | 0 | 18 | 16.5 | 11.775
19 | 20 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.211 | 0.07 | 100 | 0 | 19 | 0 | 0
20 | 21 | Fixed | 1 | 0.5 | 5 | 0.5 | 0.342 | 0.113 | 100 | 0 | 20 | 0.316 | 0.212
21 | 22 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.014 | 0.005 | 100 | 0 | 21 | 37.983 | 27.1
22 | 23 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.159 | 0.053 | 100 | 0 | 22 | 1.762 | 1.184
23 | 24 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.346 | 0.115 | 100 | 0 | 23 | 0 | 0
24 | 25 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.749 | 0.248 | 100 | 0 | 24 | 9.39 | 6.67
25 | 26 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.309 | 0.102 | 100 | 0 | 25 | 0 | 0
26 | 27 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.173 | 0.057 | 100 | 0 | 26 | 4.667 | 3.33
2 | 28 | Fixed | 1 | 0.5 | 5 | 0.5 | 0.004 | 0.011 | 100 | 0 | 27 | 4.667 | 3.33
28 | 29 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.064 | 0.157 | 100 | 0 | 28 | 8.667 | 6.185
29 | 30 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.398 | 0.132 | 100 | 0 | 29 | 8.667 | 6.185
30 | 31 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.07 | 0.023 | 100 | 0 | 30 | 0 | 0
31 | 32 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.351 | 0.116 | 100 | 0 | 31 | 0 | 0
32 | 33 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.839 | 0.282 | 100 | 0 | 32 | 0 | 0
33 | 34 | Fixed | 0 | 0.5 | 5 | 0.5 | 1.708 | 0.565 | 100 | 0 | 33 | 4.582 | 3.26
34 | 35 | Fixed | 0 | 0.5 | 5 | 0.5 | 1.474 | 0.487 | 100 | 0 | 34 | 6.501 | 4.549
3 | 36 | Fixed | 1 | 0.5 | 5 | 0.5 | 0.004 | 0.011 | 100 | 0 | 35 | 1.92 | 1.29
36 | 37 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.064 | 0.157 | 100 | 0 | 36 | 8.667 | 6.185
37 | 38 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.105 | 0.123 | 100 | 0 | 37 | 8.667 | 6.185
38 | 39 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.03 | 0.036 | 100 | 0 | 38 | 0 | 0
39 | 40 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.002 | 0.002 | 100 | 0 | 39 | 8 | 5.709
40 | 41 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.728 | 0.851 | 100 | 0 | 40 | 8 | 5.709
41 | 42 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.31 | 0.362 | 100 | 0 | 41 | 0.392 | 0.325
42 | 43 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.041 | 0.048 | 100 | 0 | 42 | 0 | 0
43 | 44 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.009 | 0.012 | 100 | 0 | 43 | 2 | 1.427
44 | 45 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.109 | 0.137 | 100 | 0 | 44 | 0 | 0
45 | 46 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.001 | 0.001 | 100 | 0 | 45 | 3.076 | 8.787
4 | 47 | Fixed | 1 | 0.5 | 5 | 0.5 | 0.003 | 0.008 | 100 | 0 | 46 | 3.076 | 8.787
47 | 48 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.085 | 0.208 | 100 | 0 | 47 | 0 | 0
48 | 49 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.29 | 0.709 | 100 | 0 | 48 | 26.35 | 18.8
49 | 50 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.082 | 0.201 | 100 | 0 | 49 | 28.226 | 91.492
8 | 51 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.093 | 0.047 | 100 | 0 | 50 | 128.226 | 91.492
51 | 52 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.332 | 0.111 | 100 | 0 | 51 | 13.512 | 9.442
9 | 53 | Fixed | 1 | 0.5 | 5 | 0.5 | 0.174 | 0.089 | 100 | 0 | 52 | 1.202 | 0.894
53 | 54 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.203 | 0.103 | 100 | 0 | 53 | 1.449 | 1.162
54 | 55 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.284 | 0.145 | 100 | 0 | 54 | 8.787 | 6.322
55 | 56 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.281 | 0.143 | 100 | 0 | 55 | 8 | 5.708
56 | 57 | Fixed | 0 | 0.5 | 5 | 0.5 | 1.59 | 0.534 | 100 | 0 | 56 | 0 | 0
57 | 58 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.784 | 0.263 | 100 | 0 | 57 | 0 | 0
58 | 59 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.304 | 0.101 | 100 | 0 | 58 | 0 | 0
59 | 60 | Fixed | 1 | 0.5 | 5 | 0.5 | 0.386 | 0.117 | 100 | 0 | 59 | 0.667 | 24.025
60 | 61 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.508 | 0.256 | 100 | 0 | 60 | 0 | 0
61 | 62 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.974 | 0.05 | 100 | 0 | 61 | 414.667 | 295.91
62 | 63 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.145 | 0.074 | 100 | 0 | 62 | 10.667 | 7.612
63 | 64 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.711 | 0.362 | 100 | 0 | 63 | 0 | 0
64 | 65 | Fixed | 0 | 0.5 | 5 | 0.5 | 1.041 | 0.53 | 100 | 0 | 64 | 75.67 | 53.873
11 | 66 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.201 | 0.061 | 100 | 0 | 65 | 19.67 | 13.912
66 | 67 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.005 | 0.002 | 100 | 0 | 66 | 6 | 4.282
12 | 68 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.739 | 0.244 | 100 | 0 | 67 | 6 | 4.282
68 | 69 | Fixed | 0 | 0.5 | 5 | 0.5 | 0.005 | 0.002 | 100 | 0 | 68 | 9.333 | 6.66
11 | 43 | Added | 1 | 0.5 | 5 | 0.5 | 0.5 | 0.5 | 100 | 25 | 69 | 9.333 | 6.66
13 | 21 | Added | 1 | 0.5 | 5 | 0.5 | 0.5 | 0.5 | 100 | 25
15 | 46 | Added | 1 | 0.5 | 5 | 0.5 | 1 | 1 | 100 | 25
50 | 59 | Added | 1 | 0.5 | 5 | 0.5 | 2 | 2 | 100 | 25
27 | 65 | Added | 1 | 0.5 | 5 | 0.5 | 1 | 1 | 100 | 25
0 | 28 | Added | 1 | 0.5 | 5 | 0.5 | 0.001 | 0.001 | 150 | 25
0 | 47 | Added | 1 | 0.5 | 5 | 0.5 | 0.001 | 0.001 | 150 | 25
0 | 53 | Added | 1 | 0.5 | 5 | 0.5 | 0.001 | 0.001 | 150 | 25
;
;

## Sis33
Parameter | Value
Lifetime of branches. | 25
Upper bounds for the absolute value of {$\Delta_{ij,t}^V$} | 20
Cost coefficients for load shedding | 2
Cost coefficients expected energy non supplied | 0.008
Cost coefficient for the energy supplied substation | 0.0002
Interest rate. | 0.07
Years into each stage | 10
Lower voltage limit | 0.95
Upper voltage limit | 1.05
Power Factor | 0.9
Nominal voltage | 12.66
Demand factor of load level | 0.83
Number of discretizations | 20
*** costs are expression in K$
*** costs are expression in K$
From | To | Type of branch | Switching | Durations of the switching-only interruptions (h) | Durations of the repair-and-switching interruption (h) | Failure rate of branch | Resistence (Ω) | Reactance(Ω) | Maximum current flow magnitude (A) | Cost coefficients for the installation | Node | Apparent power demand (kVA)
101 | 1 | Fixed | 1 | 2.5 | 5 | 0.47 | 0.0922 | 0.047 | 300 | 0 |  | First planning period | Second planning period | P | Q
1 | 2 | Fixed | 1 | 2.5 | 5 | 0.47 | 0.493 | 0.2511 | 300 | 0 | 101 | 0 | 0 | 0 | 0
2 | 3 | Fixed | 1 | 2.5 | 5 | 0.47 | 0.366 | 0.1864 | 300 | 0 | 1 | 117 | 234 | 105.3 | 50.9991
3 | 4 | Fixed | 1 | 2.5 | 5 | 0.47 | 0.3811 | 0.1941 | 300 | 0 | 2 | 99 | 198 | 89.1 | 43.1531
4 | 5 | Fixed | 1 | 2.5 | 5 | 0.47 | 0.819 | 0.707 | 300 | 0 | 3 | 145 | 290 | 130.5 | 63.204
5 | 6 | Fixed | 1 | 2.5 | 5 | 0.47 | 0.1872 | 0.6188 | 300 | 0 | 4 | 68 | 136 | 61.2 | 29.6405
6 | 7 | Fixed | 1 | 2.5 | 5 | 0.47 | 0.7114 | 0.2351 | 300 | 0 | 5 | 64 | 128 | 57.6 | 27.897
7 | 8 | Fixed | 1 | 2.5 | 5 | 0.47 | 1.03 | 0.74 | 300 | 0 | 6 | 224 | 448 | 201.6 | 97.6393
8 | 9 | Fixed | 1 | 2.5 | 5 | 0.47 | 1.044 | 0.74 | 300 | 0 | 7 | 224 | 448 | 201.6 | 97.6393
9 | 10 | Fixed | 1 | 2.5 | 5 | 0.47 | 0.1966 | 0.065 | 300 | 0 | 8 | 64 | 128 | 57.6 | 27.897
10 | 11 | Fixed | 1 | 2.5 | 5 | 0.47 | 0.3744 | 0.1238 | 300 | 0 | 9 | 64 | 128 | 57.6 | 27.897
11 | 12 | Fixed | 1 | 2.5 | 5 | 0.47 | 1.468 | 1.155 | 300 | 0 | 10 | 55 | 110 | 49.5 | 23.9739
12 | 13 | Fixed | 1 | 2.5 | 5 | 0.47 | 0.5416 | 0.7129 | 300 | 0 | 11 | 70 | 140 | 63 | 30.5123
13 | 14 | Fixed | 1 | 2.5 | 5 | 0.47 | 0.591 | 0.526 | 300 | 0 | 12 | 70 | 140 | 63 | 30.5123
14 | 15 | Fixed | 1 | 2.5 | 5 | 0.47 | 0.7463 | 0.545 | 300 | 0 | 13 | 145 | 290 | 130.5 | 63.204
15 | 16 | Fixed | 1 | 2.5 | 5 | 0.47 | 1.289 | 1.721 | 300 | 0 | 14 | 61 | 122 | 54.9 | 26.5893
16 | 17 | Fixed | 1 | 2.5 | 5 | 0.47 | 0.732 | 0.574 | 300 | 0 | 15 | 64 | 128 | 57.6 | 27.897
101 | 18 | Fixed | 1 | 2.5 | 5 | 0.47 | 0.164 | 0.1565 | 300 | 0 | 16 | 64 | 128 | 57.6 | 27.897
18 | 19 | Fixed | 1 | 2.5 | 5 | 0.47 | 1.5042 | 1.3554 | 300 | 0 | 17 | 99 | 198 | 89.1 | 43.1531
19 | 20 | Fixed | 1 | 2.5 | 5 | 0.47 | 0.4095 | 0.4784 | 300 | 0 | 18 | 99 | 198 | 89.1 | 43.1531
20 | 21 | Fixed | 1 | 2.5 | 5 | 0.47 | 0.7089 | 0.9373 | 300 | 0 | 19 | 99 | 198 | 89.1 | 43.1531
101 | 22 | Fixed | 1 | 2.5 | 5 | 0.47 | 0.4512 | 0.3083 | 300 | 0 | 20 | 99 | 198 | 89.1 | 43.1531
22 | 23 | Fixed | 1 | 2.5 | 5 | 0.47 | 0.898 | 0.7091 | 300 | 0 | 21 | 99 | 198 | 89.1 | 43.1531
23 | 24 | Fixed | 1 | 2.5 | 5 | 0.47 | 0.896 | 0.7011 | 300 | 0 | 22 | 103 | 206 | 92.7 | 44.8967
5 | 25 | Fixed | 1 | 2.5 | 5 | 0.47 | 0.203 | 0.1034 | 300 | 0 | 23 | 466 | 932 | 419.4 | 203.1247
25 | 26 | Fixed | 1 | 2.5 | 5 | 0.47 | 0.2842 | 0.1447 | 300 | 0 | 24 | 466 | 932 | 419.4 | 203.1247
26 | 27 | Fixed | 1 | 2.5 | 5 | 0.47 | 1.059 | 0.9337 | 300 | 0 | 25 | 65 | 130 | 58.5 | 28.3328
27 | 28 | Fixed | 1 | 2.5 | 5 | 0.47 | 0.8042 | 0.7006 | 300 | 0 | 26 | 65 | 130 | 58.5 | 28.3328
28 | 29 | Fixed | 1 | 2.5 | 5 | 0.47 | 0.5075 | 0.2585 | 300 | 0 | 27 | 64 | 128 | 57.6 | 27.897
29 | 30 | Fixed | 1 | 2.5 | 5 | 0.47 | 0.9744 | 0.963 | 300 | 0 | 28 | 139 | 278 | 125.1 | 60.5887
30 | 31 | Fixed | 1 | 2.5 | 5 | 0.47 | 0.3105 | 0.3619 | 300 | 0 | 29 | 633 | 1266 | 569.7 | 275.9183
31 | 32 | Fixed | 1 | 2.5 | 5 | 0.47 | 0.341 | 0.5302 | 300 | 0 | 30 | 166 | 332 | 149.4 | 72.3577
7 | 20 | Added | 1 | 2.5 | 5 | 0.47 | 2 | 2 | 300 | 80 | 31 | 233 | 466 | 209.7 | 101.5623
8 | 14 | Added | 1 | 2.5 | 5 | 0.47 | 2 | 2 | 300 | 50 | 32 | 73 | 146 | 65.7 | 31.82
11 | 21 | Added | 1 | 2.5 | 5 | 0.47 | 2 | 2 | 300 | 100
17 | 32 | Added | 1 | 2.5 | 5 | 0.47 | 0.5 | 0.5 | 300 | 200
24 | 28 | Added | 1 | 2.5 | 5 | 0.47 | 0.5 | 0.5 | 300 | 150
;
;